## Slide 1: Power Cycles and Energy Storage
John C. Bean
Outline
(Written / Revised: March 2020)
How to meet our daily cycle of electrical power consumption
Today's scenario: Base Load Power Plants (24/7) + Dispatchable Power Plants (evening only)
Possible future scenario: Base Load Plants + Massive Energy Storage
Candidates for Massive Energy:
  Pumped Storage Hydro
  Hydrogen Fuel Cells
  Flywheel Energy Storage
  Compressed Air Energy Storage (CAES)
  Capacitor / Super Capacitor Energy Storage
  Battery Energy Storage
  Molten Salt Heat Energy Storage
How much of each is required for Base Load + Massive Energy Storage scenario?
More ambitious scenario of ALSO eliminating ALL non-green power sources

## Slide 2: Power Cycles and Energy Storage
I talk about the puzzle of designing future power systems
  "Puzzle," because so many factors must be balanced to:
    Provide enough affordable power
    While sustaining a high quality biosphere
We've also seen that renewables are not silver bullets
  If only because they demand huge natural resource commitments
Meaning that future power systems will have to combine different technologies
Today you will see how the natural cycles of power consumption and production
  ALSO drive the use of different technologies
    And how energy storage will become critical

## Slide 3: It all starts with this:
An Introduction to Sustainable Energy Systems: WeCanFigureThisOut.org/ENERGY/Energy_home.htm
The cycles in our consumption of electrical power (and its real time cost):
Note the almost sinusoidal cycles:
Peaking at 6pm (cook dinner, cool down/heat up house, do laundry . . . )
With amplitude of the oscillation equaling ~ 40% of peak value
www.eia.gov/todayinenergy/detail.cfm?id=12711 YELLOW midnight lines added

## Slide 4: Simplifying a little bit, over one day:
An Introduction to Sustainable Energy Systems: WeCanFigureThisOut.org/ENERGY/Energy_home.htm
We have a constant component at about 60% of the peak
Plus an oscillating component moving from there up to 100% at about 6 pm
With oscillating component's average at 80% (from its symmetry)
Meaning that time averaged total power is also about 80% of the peak power
Peak Power
60%
Midnight
Noon
Midnight
80%

## Slide 5: Or dividing these two up:
The constant "base" electrical load:
Plus a variable "dispatchable" component (so called because a dispatcher controls it?)
So we could also call Scenario #1: "Base + Dispatchable"
60% of
Peak Power
Midnight
Noon
Midnight
0%
Midnight
Noon
Midnight
40% of Peak Power
0%

## Slide 6: Scenario #1) Base Power Plants + Dispatchable Power Plants + no storage:
This is TODAY's scenario, now in almost universal use
But, of course, power companies want to minimize costs (theirs and yours)
Costs come in two principal flavors: FIXED COSTS and VARIABLE COSTS
A fixed cost is just that, something you're going to have to pay no matter what
  For power plants, the biggest are most often construction (capital) costs
    Which are then translated into ongoing mortgage / bond payments
      Which have to be paid, whatever power you are now producing
A variable cost is instead a cost that varies with the plant's power output
  Which includes the labor cost of the operators as well as fuel costs
An Introduction to Sustainable Energy Systems: WeCanFigureThisOut.org/ENERGY/Energy_home.htm

## Slide 7: The contrast between Base and Dispatchable Plants:
FIXED COSTS: For both base and dispachable plants are ~ mortgage payments
  Which depend upon building cost, mortgage interest and duration
VARIABLE COSTS:
  Base Plant = Labor & Fuel costs while power is being produced (= all the time)
  Dispatchable Plant =
    Labor & Fuel costs while power is being produced +
    Labor & Fuel costs while plant is warming up (NOT producing power) +
    Labor costs while plant is shutting down (NOT producing power) +
    Some labor costs 24/7, for security, maintenance, deliveries . . .
But for all but open-cycle-gas-turbine dispatchable plants (which don't use steam):
  Warm up time + Shut down time can easily exceed power production time!

## Slide 8
The LCOE is still going to be hugely inflated, because it still equals:
  LCOE = Levelized Cost / Energy Produced
With numerator still depending on FULL purchase/construction cost (via mortgage)
But denominator now hugely reduced: E.G., for plant operating 3 hours per day:
  Denominator reduced by (3/24) = 1/8 => LCOE increases by 8X
Which is indeed seen in the blue cost of power time variation above!
Which is WHY our gas "peaking" power is ~ 4X cost of base power

## Slide 9: Scenario #2) Add storage in place of dispatchable plants
Why pay for dispatchable power plants that sit idle almost all of the day!
INSTEAD: Choose the CHEAPEST CLEANEST TYPE(S) OF POWER PLANTS
Let them run ALL DAY AT FULL POWER (maximizing their bang / capital buck)
  Size them so their power = 80% of peak power = average daily power
And STORE EXCESS POWER produced early in the day for use later in the day
Old Scenario #1: New Scenario #2:
Peak
Power
60%
Midnight
Noon
Midnight
80%
Base load power plants
Dispatchable
load power plants
Peak Power
Midnight
Noon
Midnight
80%
Most effective power plants,
always at full power
Stored energy

## Slide 10: But how MUCH energy do we have to store early in the day?
From earlier discussion, average power per day = 80% of peak power
  So daily energy = Edaily = 0.8 Ppeak x 1 day
Assuming shape of energy stored & moved curve below is indeed sinusoidal:
  From the diagram, amplitude of the sine = (0.2 x peak power)
Then, stored early day energy = integral (from 0 to day/2) of 0.2 Ppeak Sin
= 0.2 Ppeak x day / Pi = 0.064 Ppeak x day = (0.064)(Edaily/0.8) = 8% of Edaily
Peak Power
Midnight
Noon
Midnight
80%
Most effective power plants,
always at full power
Stored energy
So we could also call Scenario #2:
"Conventional Power
+
8% Storage"

## Slide 11: U.S. energy per day value:
1) www.eia.gov/tools/faqs/faq.cfm?id=65&t=2
From the Power Plant Land and Water Requirements lecture:
  Total US energy production (2012) = 4,047,765 GW-h (1) per year
  Which translates into US energy production = 11,089 GW-h per day
So we'd need to store 8% of that early in the morning (for use later in that day):
Scenario #2 US energy storage required per day = 887 GW-h
So with that target figure in mind, what are the alternatives?
Peak Power
Midnight
Noon
Midnight
80%
Most effective power plants,
always at full power
Stored energy
887 GW-h

## Slide 12: Candidate energy storage technologies:
http://www.sandia.gov/ess/docs/other/Grid_Energy_Storage_Dec_2013.pdf
From the U.S. Department of Energy (DOE) 2013:
Current U.S. energy storage capacity:
  (ALMOST ALL of it is pumped hydro!)
Maturity of storage technologies:
NOTE WILD EXAGGERATION!
Net U.S. Hydro storage is still tiny
And it dwarfs other 3 "Deployed"
(which at BEST = 1-2 test plants)

## Slide 13: Nevertheless, sorting the more plausible/mature candidates:
An Introduction to Sustainable Energy Systems: WeCanFigureThisOut.org/ENERGY/Energy_home.htm
Which fall into two categories based on naturally different figures of merit
Energy storage SYSTEMS = Multi-component plants, spread over hectares:
a) Pumped Hydro Energy Storage
b) Hydrogen Fuel Cell Energy Storage
c) Flywheel Energy Storage
d) Compressed Air Energy Storage (CAES)
Energy storage THINGS = Components that would just be massively warehoused:
e) Capacitor / Super Capacitor Energy Storage
f) Battery Energy Storage
g) Molten Salt Heat Energy Storage

## Slide 14: For each of these candidates, we need to know:
How much is required for our #2 energy storage scenario?
That is, storing 8% of early day energy for later use => 887 GW-h
For all candidates, this involves their "round trip return efficiency"
  Because energy returned = energy put in x return efficiency
For energy storage SYSTEMS, we need their plant footprint & storage capacity
  In order to work out total number of plants and size required
For energy storage THINGS we need their energy storage density (kW-h / m3)
  We could then assume, say, that they’d be warehoused ~1 meter high
  Combining => Net national size of such energy storage warehouses
And for all candidates, we need their projected levelized cost

## Slide 15: a) Energy storage via Pumped Storage Hydro (PSH)
An Introduction to Sustainable Energy Systems: WeCanFigureThisOut.org/ENERGY/Energy_home.htm
The best current way to store power
Which, in my Hydropower / Windpower lecture I represented thusly:
Small dam and reservoir
Lake/river "Power House" located far below
But data from previous lecture was incomplete, so we must slow down:

## Slide 16: The Bath County Virginia pumped hydro storage plant:
From Dominion Power's website:1
"The World's Biggest Battery" – but no numbers!
Supplies "over ½ million customers with (peak) power"
At rate "exceeding Hoover Dam"
One reservoir 1262 feet (385 m) above other reservoir
Max rate of flow back down =
  13.5 million gallons / minute (852 m3 / sec)
Area of upper reservoir = 265 acres (1.07 x 106 m2)
Its "water level fluctuates 105 feet (32 meters) during operation"
  OK, now we have finally got enough information to calculate energy stored!
1 km
1) Link to webpage: www.dom.com/about/stations/hydro/bath-county-pumped-storage-station.jsp

## Slide 17: Energy stored in Bath pumped storage energy plant:
Water's energy as it falls down into lower reservoir:
DE = M g h = rwater x (volume of water moved) x g x (height difference)
  rwater = 1000 kg / m3 g = 9.8 m / sec2
  height difference = 385 meters
  volume of water moved = (1.07 x 106 m2) (32 meters)
DE = (1000 kg / m3) (1.07 x 106 m2) (32 meters) (9.8 m / sec2) (385 m)
  = 1.29 x 1014 kg m / s2 = 1.29 x 1014 Joules
  = 1.29 x 1014 / (3,600,000,000) MW-h = 35.8 MW-h
Bath upper reservoir = 265 acres = 1.07 km2
  If lower reservoir were reduced to same size => ~ 2 km2 reservoir area

## Slide 18: Round trip energy efficiency of pumped storage hydro?
1) The Economist: www.economist.com/node/21548495?frsc=dg|a)
2) European Commission: etis.ec.europa.eu/publications/jrc-setis-reports/pumped-hydro-energy-storage-potential-transformation-single-dams
3) NREL: www.nrel.gov/docs/fy14osti/60806.pdf
Its largely limited by the HUGE electrical motor/generators/turbines required
  Motors drive the turbines driving the water UP the hill, then:
  Water turns turbines driving generators as it falls back DOWN
But some power may also be lost by turbulence-induced heating of the water itself
Overall power recovery, after accounting for all possible losses?
  Various sources give efficiencies from 70% 1 to 85% 2
  I'll go with the NREL study 3 number: 80% efficiency

## Slide 19: b) Fuel cell based energy storage:
U.S. National Renewable Energy Lab: "Analysis of Hydrogen and Competing Technologies for Utility-Scale Energy Storage"
http://www.nrel.gov/docs/fy10osti/47547.pdf
Idea as depicted in an NREL presentation: 1

## Slide 20: Fuel cell based storage has three stages:
An Introduction to Sustainable Energy Systems: WeCanFigureThisOut.org/ENERGY/Energy_home.htm
- Electrochemical cell # 1 uses electrical energy to electrolyze water:
  H2O + electrical energy => H2 + ½ O2
- Gaseous H2 (and possibly O2) are then stored in pressurized tanks
- When energy is needed, gases are sent into Electrochemical cell #2:
  H2 + ½ O2 => H2O + electrical energy
ONE electrochemical cell COULD do both things (~ charging/discharging of battery)
  But, apparently to optimize designs, input & output cells are separate
ALTERNATIVE: Stored H2 is instead sent to a gas turbine generator
  Eliminating fuel cell #2
    Likely less efficient but also likely reducing capital cost

## Slide 21: Fuel cell energy storage numbers?
From earlier Batteries and Fuel cell lecture:
What about energy storage density? It's very complicated:
  "Storage" is in tanks, but RATE of energy storage and release
    Will depend on size of input and output electrochemical cells
NREL's design studies are for 300 MW-h storage plants
But are now storing energy from single 10 kW wind turbine (i.e. ~ 50 kW-h)
Poor round trip efficiencies:
Only 30-35% !
U.S. National Renewable Energy Lab: "Hydrogen for Energy Storage Analysis Overview"
http://www.nrel.gov/hydrogen/pdfs/48360.pdf

## Slide 22: c) Flywheel based energy storage:
Maximum possible energy stored:
  Emax = K x M x s / r
    K = "flywheel shape factor"
    M = flywheel mass
    s = tensile strength of material
    r = density of material
Why doesn't formula contain rotation speed? And why include tensile strength?
  Because strategy is to run flywheel so fast it almost tears itself apart!
    Thus almost-destructive-speed is what formula seemingly assumes
Round trip energy recovery efficiency? Energy is lost to heat in rotation bearings
  Conventional bearings: "20-50% energy loss in two hours"
  Magnetic levitation bearings: 85% round trip energy efficiency
https://en.wikipedia.org/wiki/Flywheel_energy_storage

## Slide 23: Flywheel energy storage numbers?
1) http://energy.gov/sites/prod/files/2015/05/f22/Beacon-Power-Flywheel-Aug2013.pdf
2) http://www.theguardian.com/environment/2015/apr/08/new-energy-storage-plant-could-revolutionise-renewable-sector
3) http://www.rte.ie/news/business/2015/0326/689945-renewable-energy-storage/
http://schwungrad-energie.com/projects/rhode-hybrid-test-facility/
Web search produced information on only two experimental grid storage projects:
  Beacon Power in Hazle Township, Pennsylvania – completion 2015 (?) 1
  Rhode, County Offalay, Ireland – completion 2017 2-4
Data: Storage targets: Beacon 25 kW-h / Rhode 2 MW-h
  Pennsylvania: 200 flywheels (as depicted at right)
  Ireland: Projected efficiency: 85-90%
  Carbon fibers / magnetic bearings / vacuum
Size? / Power storage density? Found no direct data
  But from this picture is of Irish site 3
  Footprint: ~ 2 hectares = 0.02 km2

## Slide 24: d) Compressed air energy storage (CAES):
http://www.powermag.com/revived-energy-storage-technology-offers-major-grid-benefits/
Idea is potentially large scale:
  Compress air into tank or reservoir / Release air to drive turbine generator
<= Natural Gas in ?
(I'll return to this!)

## Slide 25: Most sources make CAES sound simple - It isn't!
It sounds like you just need to invoke the Ideal Gas Law:
  P V = n R T where R = the ideal gas constant
But rework this and you can spot a problem: P = n R (T/V)
  So if you increase the pressure of a gas (P), what happens?
  Does temperature (T) increase? Does volume (V) decrease? OR both?
REALITY CHECK: Try touching an air compressor, or even a bicycle tire pump
  Actually don't, you'll burn your hand because compressing gas => heat
Refrigerators, air conditioners, and heat pumps are ALL partially based on:
  - Fact that pressurizing gases HEATS them
  - Fact that depressurizing gases COOLS them
An Introduction to Sustainable Energy Systems: WeCanFigureThisOut.org/ENERGY/Energy_home.htm

## Slide 26: Faced by this reality, Wikipedia et al. ignore it
1) https://www.princeton.edu/pei/energy/publications/texts/SuccarWilliams_PEI_CAES_2008April8.pdf
2) http://content.lib.utah.edu/utils/getfile/collection/etd2/id/86/filename/1430.pdf
3) https://www.eeh.ee.ethz.ch/uploads/tx_ethpublications/Samaniego_2010.pdf
They pretend temperature stays constant, allowing them to use only Ideal Gas Law
  But this also makes calculation of CAES efficiency impossible!
RIGHT thing to do is instead add a 2nd relationship: P V m = constant
  This squirrely relationship describes a "Polytropic Process"
In it, the exponent m depends on the "heat capacity" of the gas
  = D Energy that must be added to raise gas temperature by one degree
If heating is "reversible" (D Entropy = 0), heat capacity is constant => m is constant
THEN polytropic equation can be substituted into ideal gas law to produce:
  Description of how pressurization changes BOTH V and T
    => Efficiency limits of Compressed Air Storage (CAES) 1-3

## Slide 27: Challenge of heat loss => Multiple CAES versions:
The main ones are: DIABATIC CAES and ADIABATIC CAES
But what the heck do diabatic and adiabatic mean?
  A quick Google search on "adiabatic" (= non-diabatic):
But Heat = Energy
  So heat leaving a Compressed Air Energy Storage System = Energy lost
Nevertheless, only diabatic (heat-loosing) CAES has been tried to date!
An Introduction to Sustainable Energy Systems: WeCanFigureThisOut.org/ENERGY/Energy_home.htm

## Slide 28: Contrasting the two main CAES approaches:
DIABATIC CAES (simple CAES) releases heat of compression to atmosphere
  Which means that heat for re-expansion must come from other sources
  If you've got plenty of time to wait, atmosphere can resupply the heat
    But you DON'T have time to wait with grid energy storage thus:
  Heat for re-expansion is instead supplied by burning natural gas
    => LOW NET EFFICIENCY (total energy out / total energy put in)
    THIS is scheme shown in preceding (and almost all other) CAES figures
ADIABATIC CAES traps both air and heat (as it is released)
  This requires tanks/cavities that are BOTH pressure-tight AND heat-tight
    So that stored heat can later be applied to re-heating & expanding air
    => MUCH higher energy storage efficiencies, theoretically, up to ~ 100%

## Slide 29: Compressed air energy storage numbers?
https://www.rwe.com/web/cms/mediablob/en/391748/data/364260/1/rwe-power-ag/innovations/Brochure-ADELE.pdf
There are only two existing CAES plants worldwide, both diabatic (= heat wasting)
  Huntorf Germany (42% efficient), McIntosh Alabama (54% efficient)
But a large new adiabatic (heat trapping) plant is being built: German "ADELE"
Liberated heat is stored in above-ground tanks
By warming the liquids they contain
While compressed gas goes to buried caverns
These are recombined to expand gas
Design goals (upon planned completion in 2018):
- Round trip energy efficiency: 70%
- Energy Storage: 1000 MW-h
- Footprint: ~ 1 hectare = 0.01 km2

## Slide 30: Did the ADELE CAES project achieve its 70% efficiency goal?
1) "Electricity storage with adiabatic compressed air energy storage: Results of the BMWi-project ADELE-ING" https://ieeexplore.ieee.org/document/8278771
In December of 2019, I searched the web for an answer
  To my surprise, post 2017 information about ADELE was virtually non-existent
A few CAES review articles suggested that ADELE had achieved its 70% efficiency
  Their apparent source was a single 2017 conference paper about ADELE
    which stated in its abstract: 1
  "After its completion in summer 2017 main achievements include the confirmation of a round-trip efficiency of about 70%"
But within that paper, the relevant section discussed only modeled results, about alternate technologies, none even identified as being relevant to ADELE:
  "Thermodynamic calculations for different plant calculations and TES technology options confirm a substantial cost reduction potential and improved operation flexibility, albeit with an acceptable decrease in efficiency compared to the adiabatic process. Depending on the specific system configuration and the level of permissible costs the round-trip efficiency ranges from 60 to 70% and somewhat above, with CAPEX below 280 €/kWh"

## Slide 31: Another 2017 paper stated ADELE was on hold (possibly not even complete)
1) "Overview of Compressed Air Energy Storage and Technology Development" http://wrap.warwick.ac.uk/91858/7/WRAP-overview-compressed-air-energy-storage-technology-development-Wang-2017.pdf 2) https://www.eia.gov/todayinenergy/detail.php?id=6910
As published in the journal Energies (and posted by the University of Warwick) 1
  That article's (complete) discussion of ADELE reads:
  "In Germany, as shown in Figure 15, the world’s first large-scale AA-CAES project - ADELE - with 70% cycle efficiency cycle efficiency has been designed by RWE Power, General Electric and other partners. The aim of this project is to optimize the co-existence and smooth interaction of the individual energy sources, especially for wind power. It is planned to have 1 GWh storage capacity and be capable of generating up to 200 MW, said the RWE power. The ADELE project could provide backup capacity within a very short time and replace forty state-of-the-art wind turbines for a period of 5 h. The project is now on hold due to uncertain business conditions [61]."
Note that paragraph's recurrent use of future tense AND its final sentence
If that did not confuse matters enough, when I clicked on the link provided in reference [61], I was taken to a U.S. EIA webpage which not only contained zero information about CAES, much less about ADELE. Further, that webpage was dated "June 29, 2012" (i.e., years before ADELE's construction even began).
Actual status of ADELE (or Adiabatic CAES in general)? Heck if I can figure it out!

## Slide 32: e) Energy storage via Capacitors or Super-Capacitors
As mentioned in an earlier lecture, capacitors sidestep Maxwell's 1st equation:
Trying to push more charge into an object doesn’t really work:
Unless you fold the two plates over on top of one another:
No longer need charge balance on each plate
Excess +’s on top plate don’t like one another
But repulsion's balanced by attraction to -’s below
Amount of charge stored is proportional to the pushing voltage: Q = C V (1)
Constant (C) = "Capacitance" of the capacitor - It increases the closer the plates are:
  Capacitance = Area x (dielectric constant of material in gap) / (gap thickness)
C = e Area / d (2)
An Introduction to Sustainable Energy Systems: WeCanFigureThisOut.org/ENERGY/Energy_home.htm
+
-
+
-

## Slide 33: But how much energy can a capacitor store?
Power of any type = Energy flow => P = DE / Dt (3)
But electrical power = voltage x current = voltage x (charge flow)
  Charge flow into a capacitor = DQ / Dt (change in charge stored per time)
  So power into a capacitor is: Pcapacitor = V x (DQ / DT) (4)
Equations (3) and (4) BOTH give the power and are thus equal:
  DE / Dt = V x (DQ / DT) Or in calculus terms: dE/dt = V dQ/dT
But from equation (1), Q = CV, substituting this in: dE/dt = C V dV/dT
Integrating over the capacitor's charging time: Energy capacitor = ½ C V 2
Doubled voltage applied to a capacitor => Quadrupled energy stored
An Introduction to Sustainable Energy Systems: WeCanFigureThisOut.org/ENERGY/Energy_home.htm

## Slide 34: Design of a SUPER CAPACITOR:
Here we want huge energy storage per volume = energy storage density
Volume capactior = Area capacitor x Thickness capacitor
Simple capacitor: Gray = metal plates White = insulator
Thickness capacitor = 2 T plate + T insulator
Then Energy stored in this stacked capacitor per volume is
Capacitor energy density = C V 2 / [2 x A x (2 Tplate + T insulator)]
So thinning down both the plates and insulators is a good idea, however:
Plates have to be thick enough that electron flow won't overheat them
Insulator has to be thick enough that electrons cannot jump through it

## Slide 35: This all suggests use of ultrathin nano materials
Which might allow for capacitors using single atom thick plates and insulators
http://graphene.nus.edu.sg/barbaros/

## Slide 36: But while there are extraordinarily good nano metals for the plates
Nano insulators are NOT exceptionally good at blocking electron flow
Key phenomenon is called dielectric breakdown
  Which occurs when the electric field across insulator exceeds ξ breakdown
  Electrons then arc through, irreversibly damaging the insulator!
But electric field in insulator = Capacitor voltage / Thickness insulator = V / T insulator
To avoid breakdown, T insulator must thus increase in proportion to voltage used
But from earlier formula, energy stored in a capacitor increases as voltage squared
So despite need for thicker insulators
  It still makes sense to use higher voltages in these capacitors
    As a conveniently "high" voltage, let's choose 110 volts (DC)

## Slide 37: Calculating required insulator thickness:
1) Nano Research, August 2013, Volume 6, Issue 8, pp 602-610
2) Journal of Physics: Conference Series 471 (2013)
Choosing a nano insulator from the above figure: hexagonal boron nitride:
  For h-BN, ξ breakdown is 700-900 MV / meter 1,2
For our voltage choice of 110 volts (DC) if we use h-BN for insulator then:
  For no sparks, need T h-BN > 110 Volts / (700 MV/m) ~ 160 nanometers
  For a safety margin, choose T h-BN insulator = 200 nanometers

## Slide 38: Then calculating this "nano" capacitor's energy density:
1) Journal of Physics: Conference Series 471 (2013)
Capacitor energy density = C V 2 / [2 x Area x (T plate + T insulator)]
Where: C = e Area / T insulator
And for our choice of h-BN insulator using 110 VDC:
T h-BN insulator = 200 micron = 10-6 m
T insulator >> T plate
e h-BN = (3 to 4) x eo (1) ~ 30 x 10-12 s4 Amp2 / kg m3
Capacitor energy density ~ (e A / T insulator) V 2 / (2 A T insulator) = e V 2 / 2 Tinsulator2
= (3x10-11 s4 Amp2 / kg m3) (110 volts)2 / 2 (0.2x10-6 m)2
= (3x10-11)(1.2x104)(0.5)(2.5x1013)(s2 J2/kg-m5) = 4.5 MJ/m3 = 1.25 kW-h/m3
Likely efficiencies: ~ 100%
200 nm
Area

## Slide 39: f) Energy storage via Super-Batteries
From note set on Batteries and Fuel Cells (pptx / pdf / key),
  the top candidate might be flow batteries:
Which, recall, have this strange and complex configuration:
With two different electrolytes circulated in (via pumps) from external tanks
  To a central cell with an "ion selective membrane"
    Plus simple metal electrodes to either side

## Slide 40: Molten sodium beta alumina batteries were a second candidate
Figure: Electrochemical Energy Storage for Green Grid, Yang et al., Chemical Reviews 111, 3577–3613 (2011)
1) http://en.wikipedia.org/wiki/Molten_salt_battery
With overall structure:
- Central (anode) reservoir of molten sodium (green)
- Membrane capable of passing Na+ ions (gray)
  Typically: Al2O3 "beta alumina" ceramic
- Surrounding (cathode) outer cylinder (orange)
  Typically: Sulfur / Sodium Sulfide (Na2Sx)
  In the central anode: At the outer cathode:
  2 Na => 2 Na+ + 2 e- x S + 2 Na+ + 2 e- => Na2Sx
With Na+ ions formed in anode migrating through beta alumina toward cathode

## Slide 41: Lithium ion batteries were a third candidate:
During CHARGING, Li is actually transferred from inside cathode to inside anode
-
Anode:
Li absorbing
and deionizing
Cathode:
Li dissolving and ionizing
+
+
-
+
-
-
Anode:
Li desorbing
and ionizing
Cathode:
Li absorbing and deionizing
+
+
-
+
-
DISCHARGE reverses this: Li transferred from inside the anode to inside cathode:

## Slide 42: Comparative battery energy density data on all of these:
Left) http://www.sc.ehu.es/sbweb/energias-renovables/temas/almacenamiento/almacenamiento.html
Right (compacted version of): http://www.nrel.gov/hydrogen/pdfs/48360.pdf
Ion flow energy density = Up to 30 kW-h / m3 at ~ 73% efficiency
Molten Na energy density = Up to 270 kW-h / m3 at ~ 77% efficiency
Li Ion battery density = Up to 350 kW-h / m3
Li Ion
Molten Sodium
Flow
(vanadium redox)

## Slide 43: g) Heat energy storage via Molten Salts
1) http://www.nrel.gov/docs/fy13osti/58595.pdf
Best batteries returned ~ 80% of electrical energy
  Using electrical power in => electrical storage => electrical power out
Molten salts return only about 70% of heat energy
  A 10% drop (compared to batteries) sounds significant
    But while batteries are expensive, salt is cheap!
      We might even mine AND store heat in the original SALT MINES!
NREL - Halotechnics Molten Salt Energy Storage Test Project, Emeryville CA:
  35.45 kW-h stored in 0.19 m3 of salt, returning 25.1 kw-h (71%) 1
Which gives:
  Salt energy storage density = 25.1 kW-h/0.19 m3 = 132 kW-h/m3

## Slide 44: FINALLY (!): Using ALL of the data from above:
An Introduction to Sustainable Energy Systems: WeCanFigureThisOut.org/ENERGY/Energy_home.htm
To compute the impact of the most promising storage technologies when used in:
Scenario #2 = Conventional Power + 8% Storage:
Peak Power
Midnight
Noon
Midnight
80%
Most effective power plants,
always at full power
Stored energy
887 GW-h

## Slide 45: Projected numbers for nation-wide energy storage SYSTEMS:
Pumped Storage Hydro based energy storage SYSTEMS: 80% efficiency
  Bath PSH = 35.8 MW-h occupying ~ 2 km2
  Number of plants: 887 GW-h / 35.8 MW-h = 24,781 plants
  Cumulative national footprint: (~ 25,000) x (~ 2 km2) => ~ 50,000 km2
Fuel Cell based energy storage SYSTEMS: 30-35% efficiency
  ”Planned” (future) plant capacity = 300 MW-h:
    Number of plants: 887 GW-h / 300 MW => 2,956 plants
  Current test plant = 50 MW-h, no info given on plant sizes
    Number of plants: 887 GW-h / 50 MW => 17,740 plants
  Cumulative national footprint: Not enough information given = ? km2

## Slide 46: Projected numbers for nation-wide energy storage SYSTEMS (cont’d):
Flywheel based energy storage SYSTEMS: 85-90% efficeint
  Current projects = 2 MW-h occupying ~ about 2 hectares
  Number of plants: 887 GW-h / (2 MW-h) => 443,500 plants
  Cumulative national footprint: ~ 90,000 hectares => 9000 km2
Adiabatic compressed air based energy storage SYSTEMS: 70% efficient
  Adiabatic plant (under construction) = 1000 MW occupying ~ 1 hectare
  Number of plants: : 887 GW-h / (1 GW-h) => 886 plants
  Cumulative national footprint: ~ 900 hectares => 9 km2
Now moving onto energy storage THINGS:

## Slide 47: Projected numbers for nation-wide energy storage THINGS:
An Introduction to Sustainable Energy Systems: WeCanFigureThisOut.org/ENERGY/Energy_home.htm
Based on assumptions: Volume = 887 GW-h / (energy storage density)
  Converted to a footprint by assuming these are piled ~ 1 m high in warehouses
Battery based energy storage THINGS: 70-80% efficient
  Energy Storage Density – Flow Batteries: 30 kW-h/m3
    Cumulative volume => footprint: 29 x 106 m3 => 29 km2
  Energy Storage Density – Molten Sodium Batteries: 270 kW-h/m3
    Cumulative volume => footprint: 3.3 x 106 m3 => 3.3 km2
  Energy Storage Density - Lithium Ion Batteries: 350 kW-h/m3
    Cumulative footprint: 2.5 x 106 m3 = 2.5 km2

## Slide 48: Projected numbers for nation-wide energy storage THINGS (cont’d):
An Introduction to Sustainable Energy Systems: WeCanFigureThisOut.org/ENERGY/Energy_home.htm
Capacitor based energy storage THINGS: likely nearly 100% efficient
  Energy Storage Density – h-BN insulator : 1.25 kW-h/m3
  Cumulative volume => footprint: 1.26 x 108 m3 => 126 km2
Molten Salt based heat energy storage THINGS: 70% efficient
  Energy Storage Density: 132 kW-h/m3
  Cumulative volume => footprint: 6.7 x106 m3 => 6.7 km2
However, if you could get them to efficiently store heat,
Salt Caverns might be a much better idea for cheap/large-scale storage

## Slide 49: Leading to the somewhat surprising result:
An Introduction to Sustainable Energy Systems: WeCanFigureThisOut.org/ENERGY/Energy_home.htm
In contrast to note set Power Plants Requirements: Land & Water (pptx / pdf / key)
For this Scenario #2 = Conventional Power + 8% Storage
Land requirements of essentially all storage technologies are NOT excessive!
Indeed, especially for the technologies located primarily underground:
  Surface ground use and overall environmental impact might be small
So WHY don't we already make extensive use of energy storage?
The answers must lie in:
The Cost of Grid Scale Energy Storage

## Slide 50: NREL estimates of energy storage LCOEs:
U.S. National Renewable Energy Lab: "Hydrogen Energy Storage Overview"
http://www.nrel.gov/hydrogen/pdfs/48360.pdf
From a 2010 NREL presentation (with dashed lines giving anticipated 2015 costs):
Figure uses units of ¢/kW-hr rather than more common units of $/MW-h:
1¢/kW-hr => $10/MW-h (i.e. multiply by ten and change units)
100$/MW-h

## Slide 51: An independent corporate study:
http://dotyenergy.com/PDFs/Doty-90377-Storage-ASME-ES10.pdf
"Projections of the Levelized Cost Benefit of Grid Scale Energy Storage Options"
  From a 2010 conference paper presented by Doty Energy Corp.
Final column gives levelized cost due to storage using the indicated technology

## Slide 52: A comparison of those data (all in $/MW-h):
Storage Technology
Pumped Storage Hydro
Fuel Cell
V redox battery
Adiabatic CAES
Li ion battery
Flywheel
Lead Acid battery
NaS battery
NiCd battery
Ultra Capacitors
NREL LCOE
2010
130-180
100-600
220-500
100-165
220-320
480-1030
Doty LCOE
2010
56
51
162
167
532
181
774
2910
NREL LCOE
~ 2015
130
240-280
280
100
250
830

## Slide 53: Quick analysis of storage LCOE's:
Pumped storage hydro (PSH / UPSH) is cheapest: ~ $50 / MW-h
Fuel cell storage: Doty: Comparable to PSH NREL: 4-5 X PSH
Adiabatic CAES & best battery storage ~ 2-3 X PSH = $100-150 / MW-h
Storage LCOE would be ADDED to energy's production LCOE = $70-150 / MW-h
  Seemingly at least doubling or tripling the total cost of energy!
But not really, because under Scenario #2:
  Storage cost is added to only to the ~ 8% of power we need to store
And competition = Scenario #1 evening power, already 2-4X more expensive!
Thus some experts say storage could
be competitive within five years

## Slide 54: NEW Scenario 3: Use of ONLY “green” sustainable power sources
An Introduction to Sustainable Energy Systems: WeCanFigureThisOut.org/ENERGY/Energy_home.htm
“Greenest” of renewable energy sources don't produce energy all of the time:
  Examples include solar power, wind power, tidal power
And when they DO produce, it's not when we most need their production!
This, again, is how we LIKE to consume energy:
www.eia.gov/todayinenergy/detail.cfm?id=12711 YELLOW midnight lines added

## Slide 55: These are data on actual wind speeds vs. time of day
TEXAS: www.seco.cpa.state.tx.us/publications/renewenergy/windenergy.php
ONTARIO CANADA: www.omafra.gov.on.ca/english/engineer/facts/03-047.htm
NETHERLANDS: www.ekopower.nl/wind-energy-monitoring-data-logger-data-processing.htm
WISCONSIN: www.windpowerweather.com/history?date=last2days

## Slide 56: Which, recalling that wind energy goes as wind velocity cubed:
An Introduction to Sustainable Energy Systems: WeCanFigureThisOut.org/ENERGY/Energy_home.htm
Would lead to a typical wind energy versus time of day plot something like this:
  (~ doubled afternoon wind speed => ~ 23 X wind power)
Thus, with wind energy peaking sharply in the late afternoon, we'd get power like:
100%
Midnight
Noon
Midnight

## Slide 57: Solar energy peaks midday, but also varies by season:
An Introduction to Sustainable Energy Systems: WeCanFigureThisOut.org/ENERGY/Energy_home.htm
Starts at sunrise, peaks at about noon, ends at sunset
And lasts longer and is more intense in the summer:
100%
Midnight
Noon
Midnight
Summer
Winter

## Slide 58: Wholesale use of renewables => HUGE NEED for storage!
What we now need/want in the way of daily power:
What we'd get from a wind plant: What we'd get from a solar plant:
100%
Midnight
Noon
Midnight
100%
Midnight
Noon
Midnight
100%
Midnight
Noon
Midnight

## Slide 59: Let me (somewhat crudely) approximate either as half sine wave:
Area under half sinusoid = Amplitude x day / Pi = Ppeak_renewable x day / Pi
But if this to be all our power, this must = 80% Ppeak_use x day
Implying Ppeak_renewable = 0.8 Pi Ppeak_use = 2.5 Ppeak_use
Peak
Power Use
Midnight
Noon
Midnight
80%
Power of Renewable at Peak

## Slide 60: Whoops, so wind energy production would have to be more like:
But I now need to store and shift ALL energy above green "use" line!
Yellow Base ~ (0.8 Ppeak_use )(d/2) = (0.4 d)(Ppeak_renewable /2.5) = 0.16 Ppeak_renewable d
Fraction that must be stored and shifted = 1 - Yellow base / All
= 1 – (0.16 Ppeak_renewable d) / (Ppeak_renewable d day / Pi) = 1 – 0.16 Pi = 50%
Making this the ”Green (only) Sustainables + 50% Storage” scenario
Peak Power Use
Midnight
Noon
Midnight
Power of Renewable at Peak
80% of Peak Power Use
Midnight
Noon
Midnight
Power of Renewable at Peak
≈

## Slide 61: Whoops squared!
From previously having to store 8% of energy to accommodate our power use curve
If we use single "green" renewable (i.e. neither hydro or nuclear), we would have to:
  Store and shift 50% of energy to accommodate our power use curve
Switch to renewables => Need to increase storage by ~ 6X
(vs. storage Scenario #2 which just eliminated evening "peaking" power plants)
Two renewables, peaking at different times (e.g. solar and wind) help a little
  Two renewables, coming from different time zones, help a little more
But this strongly suggests that we will have to retain some 24/7 power sources
  Producing a good fraction of the present day (Scenario #1) base load
It's going to be really hard to abandon hydro & nuclear power!

## Slide 62: Credits / Acknowledgements
Some materials used in this class were developed under a National Science Foundation "Research Initiation Grant in Engineering Education" (RIGEE).
Other materials, including the "Virtual Lab" science education website, were developed under even earlier NSF "Course, Curriculum and Laboratory Improvement" (CCLI) and "Nanoscience Undergraduate Education" (NUE) awards.
This set of notes was authored by John C. Bean who also created all figures not explicitly credited above.
Copyright John C. Bean
(However, permission is granted for use by individual instructors in non-profit academic institutions)
An Introduction to Sustainable Energy Systems: WeCanFigureThisOut.org/ENERGY/Energy_home.htm